## Slide 1: News and computing activities at CC-IN2P3
FJPPL Meeting at CC-IN2P3

## Slide 2: The infrastructure issue … … is solved
Slope: 500W / day
The building of the new computer room will start very soon
We expect to get it by early 2011

## Slide 3: Capacity of new computer room
We have built a simple computing model with the following ingredients:
Serve ~40 groups with "standards needs"
Fulfill LHC computing commitments and provide first class analysis capability
Expect a very significant growth of the Astroparticle community needs (LSST for instance)
Add some services

## Slide 4: New computer room
Assume Moore law is still valid
Extrapolate up to 2019
On top of the existing computer room (1 MW)
indicated power is for computing only
power for cooling has to be added
Due to budget constraints the new computer room will have to start with a limited power
 Modular design – Easily scalable
Chilled water and electricity distribution is designed for the 2019 target value
Equipment: transformers, chillers, UPS etc… will be added later
End up with:
2011
50 racks
600 kW
2015
125 racks
1.5 MW
2019
216 racks
3.2 MW

## Slide 5: Design consideration
The 2 storey building will be devoted to computing equipment (no offices)
First storey: Services (UPS, Chillers, etc.) - 900 m2
Second Storey: Computer room - 900 m2
We decided to give up with raised floor
Every fluids will come from the top: Chilled water – Power – Network

## Slide 6
Chillers on the roof
Pumps
Inverted beams
Connection between old and new computer room + elevator

## Slide 7: Analysis farm
We are setting up a prototype analysis farm for LHC experiments
  PROOF based
  I/O intensive
  Fast turn around to speed up analysis code development
  Blade center + 16 DELL blades – 16 Thread / blade – 3 Go / Thread
    2 10 Gb/s network cards (blade interconnection and iSCSI storage
  3 SAN crates iSCSI Dell EqualLogic PS 6010XV – 20 TB
    16 600 Go 15 000 RPM SAS disks
  Connection to xrootd server
The idea is to test this setup with different configurations and to compare to other analysis farms – Requires help from experiments
The system will be extended once we have a satisfactory configuration

## Slide 8: New batch system
We have decided to stop developing our own batch system (BQS) and to migrate to a new product
A task force is working in order to propose a new batch system.
Extensive comparison work
Review of the systems adopted in other sites
Choice has been restricted to 2 products:
  SGE
  LSF
Then we will proceed to the migration…
The final choice will be done early March

## Slide 9: Grid future strategy
EGEE  EGI in a couple of months
NGI : France Grille is being setup
  8 partners
CC-IN2P3 will continue to play a central role in grid operation
  At EGI level – Grid operation portal
  At NGI level
We would also like to promote JSAGA work
  Leverage JSAGA work to improve grid accessibility

## Slide 10: Ideas…
Integration of grid and cloud framework
Well… I still have to figure out what is exactly the cloud model for particle physics
Create a France – Asia Virtual Organization / Grid
  Support for AIL applications
  Training
Could support both NAREGI and gLite

## Slide 11: Grid future strategy
Annecy
Grenoble
Lyon
TIDRA is a regional grid oriented toward data treatment
Open to any regional scientific application
Hope to open it to industrial world
Easy access is crucial…
… and difficult to setup !