## Slide 1
Modelisation of Acoustic Newtonian noise in Einstein Telescope caverns :
Application to the design of HVAC systems
L. Maurin (PhD), S. Terrien, F. Gautier
M. Barsuglia
Réunion ET France 2025
7-8 oct. 2025, IN2P3, Lyon

## Slide 2
Artist view of ET – Triangle configuration
Credits : M. Kraan
Geometry of an end cavern
Einstein Telescope (ET) - layout and sensitivity
ET design sensitivity
Order of magnitude : 10-24@10Hz
ETLF and ET HF baseline sensitivity

## Slide 3
Acoustic Noise in GW detector : what do we learn from Virgo ?
Virgo’s current air handling unit
The main acoustic source in the experimental halls comes from the Air Conditioning system
Pressure field
Inlets/outlets

## Slide 4
HVAC system
heating ventilation and air conditioning
airborne source
  responsible for acoustic noise
structure borne source
  responsible for ground/walls vibrations
Air flow
Local turbulence
Generation of acoustic
disturbances (pressure pulsations)
Acoustic radiation by inlets/outlets
Equivalent monopolar source
Horn geometry
HEPA filter
Simulation of acoustic field
Clear modal behaviour below 30Hz
Positions of inlets/outlets are key factors
inlets
outlets
Sound generation in the experimental halls

## Slide 5
Acoustic pressure ~ density fluctuations
Potential and gravity field
Modal expansion of the pressure field
Expansion of the gravity field = newtonian noise
Newtonian noise from acoustic origin – methodology for the modelling
Functional basis
Acoustic mode
amplitude
amplitude

## Slide 6
Meet Workshop, Italy, Orosei 6-10 October 2025
Acoustic Noise from air conditioning unit – Full and simplified model
harmonic pistons
Simulation
Measurement
Pressure
Outlets Acoustic flow
Inlets
Acoustic flows
Full model : ducts and room are coupled and excited by 2 pistons
Simplified model : inlets and outlets are replaced by equivalent monopoles whose flow is computed from the full model.
a selection of dominant inlets/outlets is considered only.
Good aggreement between direct measurement and simplified model !

## Slide 7
Acoustic field
Potential of gravity field
Function
Function
Modal basis
Functional basis
Modal and functional bases

## Slide 8
Acoustic field
Gravity field
Function
Function
Modal and functional bases

## Slide 9
What is the impact of the Newtonian noise on the suspended test mass?
Streamlines for the gravity field in the room in the 2D
cross-section at one meter from the ground.
Estimating the NN from a simplified model
NN is far below Virgo sensitivity
estimate of the NN of acoustic origin

## Slide 10
Acoustic modal basis of an end cavern
f1=0Hz
f2=1.2Hz
f3=2.2Hz
f4=4.3Hz
f5=4.8Hz
f6=6.3Hz
f7=6.9Hz
f8=7.1Hz
Mode count function
10
0
20
30
40Hz
50
100
200
High acoustic modal density due to the large size of the room
Remarks
  The cave is supposed to be closed... and disconnected from the tunnel(s)!
  The sound inside the tunnel is ignored, but the acoustic modal density inside is enormous (!)

## Slide 11
Functional basis for the potential expansion
f1=0Hz
f2=1.2Hz
f3=2.2Hz
f4=4.3Hz
f5=4.8Hz
f6=6.3Hz
f7=6.9Hz
f8=7.1Hz

## Slide 12
f1=0Hz
f2=1.2Hz
f3=2.2Hz
f4=4.3Hz
f5=4.8Hz
f6=6.3Hz
f7=6.9Hz
f8=7.1Hz
Functional basis for the gravity field
Numerous longitudinal modes => orientation of the NN gravity field is mostly in the laser beam direction !

## Slide 13
Configuration 1
Simulated NN of acoustic origin – effect of the inlets/outlets positions
Integration of thh Virgo sources inside the ET cavern
Test of 2 configurations for the inlets/outlets
NN level is above the sensitivity curve !!!
10-24
10-25
10-26
10-23
10-22
10-28
10-27
Configuration 2
8 inlets
4 outlets

## Slide 14
Air flow variation
Simulated NN of acoustic origin – effect of the fan rotation speed
The fan rotation speed is the most influent parameter on the noise level (power law)
Simulations for
  Virgo’s source amplitude
  2 x Virgo
  0.5 x Virgo
=> The methodology can be used to estimate the acoustic threshold
10-24
10-25
10-26
10-23
10-22
10-28
10-27

## Slide 15
Simulated NN of acoustic origin – effect of acoustic absorption
Adding acoustic absorption helps to limit NN
In practice, acoustic absorption at low frequency is very difficult to achieve
Melamine foam
Wiremesh
10-24
10-25
10-26
10-23
10-22
10-28
10-27

## Slide 16
HVAC is necessary for the thermal stability and also for the health of the operators
Acoustic noise due to HVAC induces Newtonian Noise, visible by ET
Acoustic Newtonian noise must be considered as an issue in the design of Einstein Telescope’s cavern
The developped approach can give insight
  on the geometry of caverns
  on the positions of the inlets/outlets
  on the positions of the towers
  On the specification of the HVAC
Collaboration with ETO, P. Werneke has started. Collaboration with the CERN engineers in charge of the HVAC system would be useful. How to formalize this collaboration?
Short-term perspectives
  extension to the analysis of NN of vibratory origin (vacuum pumps, cryogenic pumps …)
  Starting collaboration with C. Collette (Univ. Liege). links between NN and active control
Concluding remarks