## Slide 1
Timing, MPS and control of the beam operation at SARAF
Alexis Gaget IRFU / DIS /LDISC

## Slide 2: SARAF
1

## Slide 3: SARAF Accelerator
04
Phase 1
Phase 2

## Slide 4: Timing System
2

## Slide 5: Micro Research Finland (MRF) based
Universal Modules
  TTL 5V output
  TTL input
  Optical fiber
Industrial PC
  IFB300SAM
  IPC Kontron
  PCIe-EVR300DCS
MTCA.4
  NAT R2 crate + MCH PHYS80
  + MCH-COMEXe3
  MTCA-EVR-300U
  MTCA-EVM-300
« You don’t know MRF ? Come to the Timing Workshop on Thursday »

## Slide 6: Timing Topology
10/02/2023
Timing System, Micro Research Finland (MRF) based:
    5 EVMs
    20 EVRs
176MHz Clock + Meridian GPS (PPS, 10MHz, NTP server)
Distribute timestamping and synchronization
HEBT is not in our scope (but room planned for it)

## Slide 7: Pulse Generation
Produced by EVM sequencer

## Slide 8: Some MTCA EVR examples
EVR Injector
EVR LLRF
MTCA Backplane
MTCA Backplane

## Slide 9: Machine Protection System
2

## Slide 10: Machine Protection System
Timing (TMG) is the heart of the MPS creating or shutting the beam pulse through chopper and magnetron and being the messenger of the shutbeam event
Beam destination master (BDM) controls that conditions to get the beam to a destination are checked. Linked to all PLC all along the accelerator through Profinet
Section Beam Current Transmission is checking current of the beam all along the accelerator and compare them.

## Slide 11: Machine Protection System
During a shutbeam
  All the pulses are immediatly interrupted
  Sequence continue, but Beam Presence and Chopper pulses are masked
Shutbeam

## Slide 12: Timing + MPS
10/02/2023
Each of these EVRs is part of the MPS.
    The EVR Injector is the one that will shut down, chopper and magnetron,
    The EVR BDM is the link with the PLC BDM; requests to shut the beam will come from there.
    The EVRs LLRF will cut the RF and request a shutbeam.
    The EVRs SBCT and BPM will request a shutbeam.

## Slide 13
Use of the upstream event principle
  An input of the EVR is triggered, and an event is sent upstream and redistributed by the EVM Master to all EVRs.
Cons: Cannot use delay compensation because MPS events cannot be delayed.
=> Recently solved by Jukka: creation of a priority event that is not delayed. Presentation and demonstration during the Timing Workshop. Gabriel (CEA) has almost finished integrating this new function into the mrfioc2 EPICS driver.
Timing + MPS

## Slide 14: Section Beam Current Transmission (SBCT)
The Section Beam Current Transmission checks the beam current along the accelerator and compares the measurements (ACCTs, Faraday cups, chopper…).
MTCA IOxOS based :
                ADC3117 : 20 channels, 5 MSamples/sec, ±10 V
                DIO3118 datasheet : 16 I/O
                MTCA.4 AMC : IFC1410 (FPGA Xilinx Kintex Ultrascale + CPU PPC)

## Slide 15: Section Beam Current Transmission (SBCT)
Different functions implemented
  Current differences
  Beam Amplitude checking
  Beam On/Off management
  Etc …

## Slide 16: Section Beam Current Transmission (SBCT)
EPICS
epicsComGen or “Epics comme j’aime” : generates communication between FPGA registers and EPICS PVs
1300 PVs EPICS

## Slide 17: Beam Destination Master (BDM)
Beam destination master (BDM) controls that conditions to get the beam to a destination are checked. Linked to all PLC all along the accelerator through
Siemens PLC based
S7PLC (read) / Modbus (write) (no opc-ua yet at the time)
PLCParsertool generate communication between PLC registers and EPICS PVs

## Slide 18: Beam control
2

## Slide 19: Beam control
When the operator asks for a pilot beam (default configuration: 1 Hz, 50 µs), the following SNL sequence is launched.
Example of configuration for destination MEBT Diagnostic box 2

## Slide 20: Beam control
Example of configuration for destination MEBT Diagnostic box 2
Beam Destination master (BDM)
  Check Beam condition for a beam destination
When the operator asks for a pilot beam (default configuration: 1 Hz, 50 µs), the following SNL sequence is launched.

## Slide 21: Beam control
Beam Destination master (BDM)
  Check Beam condition for a beam destination
Section Beam Current Transportation (SBCT)
  Configure security to reach a beam destination.
Example of configuration for destination MEBT Diagnostic box 2
When the operator asks for a pilot beam (default configuration: 1 Hz, 50 µs), the following SNL sequence is launched.

## Slide 22: Beam control
Beam Destination master (BDM)
  Check Beam condition for a beam destination
Section Beam Current Transportation (SBCT)
  Configure security to reach a beam destination.
Cavity Application (CAV)
  Check that every cavity up to the beam destination is up and ready.
  A cavity is READY for operation if :
    the LLRF is ON,
    the LLRF is in regulation mode,
    the measured accelerating voltage has reached the target accelerating voltage and is stable enough,
    the external alarm is enabled.
When the operator asks for a pilot beam (default configuration: 1 Hz, 50 µs), the following SNL sequence is launched.
Example of configuration for destination MEBT Diagnostic box 2 : RFQ + 3 Rebunchers

## Slide 23: Beam control
Beam Destination master (BDM)
  Check Beam conditions for a give beam destination
Section Beam Current Transportation (SBCT)
  Set correct configuration to reach a beam destination.
Cavity Application (CAV)
  Checks that every cavity up to the beam destination is up and ready.
Max Pulse Width (MPW)
  According to the destination and inserted elements, authorize a maximum current to avoid damaging any equipment.
  For destination MEBT Diagnostic box 2 FFC , the beam hits a Fast Faraday Cup, which is a fragile equipment, so only a very low beam current is authorized.
When the operator asks for a pilot beam (default configuration: 1 Hz, 50 µs), the following SNL sequence is launched.

## Slide 24: Beam control
Beam Destination master (BDM)
  Check Beam condition for a beam destination
Section Beam Current Transportation (SBCT)
  Configure security to reach a beam destination.
Cavity Application (CAV)
  Check that every cavity up to the beam destination is up and ready.
Max Pulse Width (MPW)
  According to destination and element inserted will authorize a maximum current in order to do not damage any equipment.
Timing (TMG)
  Checks that the optical fiber network up to this destination is working properly.
When the operator asks for a pilot beam (default configuration: 1 Hz, 50 µs), the following SNL sequence is launched.

## Slide 25: Beam control

## Slide 26: Conclusion
For now it gives great satisfaction for the commissioning of the MEBT of SARAF.
SBCT is still in active development and testing.
We hope to test everything soon with the first cryomodule.
Perspective
  MRF will be used for Titan accelerator in Saclay (MPS not included this time)
  MRF + MPS architecture has been proposed for pre-project for ICONE accelerator.
(“Introduction to the software and hardware platforms for the Pre-Project of the ICONE Accelerator – Spring EPICS Meeting 2025)

## Slide 27: Merci
CEA SACLAY
alexis.gaget@cea.fr
MRF TIMING SYSTEM DESIGN AT SARAF
October 2021
DOI: 10.18429/JACoW-ICALEPCS2021-THPV022
MACHINE PROTECTION SYSTEM AT SARAF
October 2023
DOI:
10.18429/JACoW-ICALEPCS2023-THPDP102
EPICS CONTROL SYSTEM FOR BEAM OPERATION AT SARAF LINAC ACCELERATOR
September 2025
DOI:
10.18429/JACoW-ICALEPCS2025-THPD098

## Slide 28: Check Optical fiber connection
Check TX (upstream) connexion.
  Native in the driver through PV $(PREFIX):Link-Sts
Check RX (downstream) connexion
  Not native in EVR, we need to use EVM informations and knowing in which positions are connected the EVR. Indicated in the cmd of the EVR
  When more than 1 floor we need to know the « full path ». EVM Master + EVM Fanout
LLRF EVR configuration

## Slide 29: RF conditioning
Pilot Beam Mode
  Standard mode where all EVMs and EVRs are connected as one tree.
  Beam
RF Conditioning Mode
  We can dissociate any EVM from the rest to make it autonomous.
  Allows independant RF conditioning operation.
RF conditioning for cryomodule 2-3-4