## Slide 1: Design and Implementation of the CSNS-II Accelerator Control Network Management System
Kangjia Xue
Institute of High Energy Physics, CAS / China Spallation Neutron Source
Spring EPICS Collaboration Meeting 2026

## Slide 2: Background
CSNS now has about 650 online control-network devices; CSNS-II will exceed 1,500. Previously, each subsystem allocated IP addresses from its own range, which caused several problems.
CSNS-II Network Topology
Subsystems used inconsistent records, often missing information needed for operation and maintenance.
IP data was kept in Excel files, making management difficult and leaving no approval workflow.
No network access control was available.

## Slide 3: Main Functions
Network Features
Many accelerator devices, such as serial servers and power supplies, cannot request network access by themselves.
MAC-address binding is not suitable because it complicates device replacement after failures.
Accelerator networks require detailed device records, not just the IP user.
Goal: build a system for accelerator operation and maintenance, covering IP address management and network access control.
IP Address Management
Main Functions
Device Online Status
Device Location
Switch Information
Port Information
Subnet Information
Network Access Control

## Slide 4: System Architecture
System Architecture
User interface: Web-based application built with Vue.js and the PrimeVue component library.
Back-end services: Node.js and MongoDB.
Hardware interaction: Python, using the Netmiko library to connect to switches.

## Slide 5: IP Address Management
Centralized IP management — records device name, purpose, manufacturer, and model for each IP address.
IP Overview Page
Online IPs
Online Status
Unregistered IPs
Allocation Status
Port Binding
Using Subsystem
Reserved Subsystem
Device Name
Device Purpose
User
Actions

## Slide 6
Users can select an unassigned IP address and submit an application.
IP Address Application Form
User
Device Name
Device Purpose
Using Subsystem
Manufacturer
Device Model
Operating System
Maintenance Information
Switch Name
Switch Port
Remarks

## Slide 7
IP Address Application Workflow
The application and approval workflow ensures that every networked device has complete maintenance information.

## Slide 8: Switch Information Query
Static data imported by administrators.
Including information such as the name and location of the switch.
Switch IP
Switch Name
Location
Model
Manufacturer
Commissioning Date
Remarks
Actions

## Slide 9: Port Information Query
By collecting interface data and MAC tables from access switches, the system reports link status, VLAN ID, and connected MAC address for each port.
Switch Port
Link Status
Port Security
Cable ID
Binding Status

## Slide 10: Locating Connected Devices
Using IP-to-MAC mappings from the core-switch ARP table, the system maps a device to its switch port.
Because switch locations are recorded, the physical location of any connected IP address can be found directly.
Switch Dynamic Information
Registered Information
Access Switch Location
Access Switch Name
Access Switch Port

## Slide 11: Real-Time Online Status
By reading the core switch ARP table, the system can identify whether an IP address is online.
Switch Dynamic Information
Online Status
MAC Address

## Slide 12
Using Filters to Identify Abnormal Conditions.
For example, filtering for online and unassigned IP addresses identifies unauthorized devices connected to the control network and shows their physical location.
Online
Unassigned

## Slide 13: IP Online / Offline Logs
Derived from changes in the core switch ARP table.
Provides an overview of all IP online/offline events, or detailed history for a single IP addresses.
IP Address
Online / Offline
MAC Address
Time

## Slide 14: MAC Address Change Logs
Similarly, the system records MAC address changes.
Used to detect device changes.
IP Address
New MAC Address
Previous MAC Address
Time

## Slide 15: Network Access Control
Access control based on IP-port binding.
With MAC address binding, replacing a device requires re-registration.
With IP-and-port binding, a replacement device simply needs to be configured with the same IP address and connected to the same port.
Bind IP 10.1.200.58 to switch CCR5736-1 (10.1.200.13), port GigabitEthernet0/0/3

## Slide 16
IP-port binding depends on switch hardware: Huawei switches use IPSG rules, while Ruijie switches use port-security rules.
IP Address and Switch Port Binding Workflow

## Slide 17: Change Port VLAN
Unlike generic tools, this page also shows whether the port is assigned, plus the related IP address and device information.

## Slide 18: Disable / Enable Ports
Unassigned ports can be viewed and disabled on the page to reduce security risks.
Disabled Port

## Slide 19: Integration with Other Systems
For example, caPutLog mainly records the hostname of the operating host. After linking with this system, a hostname can be mapped to the exact control-room computer.

## Slide 20
The system also provides an API for AI-assisted queries.

## Slide 21: Thank You