## Slide 1: Non-intrusive Observability and Load Isolation for Critical EPICS Timing Systems at PSI
EPICS collaboration meeting - April 2026
Romain Vallotton
Paris-Saclay, 22 April 2026

## Slide 2: Agenda
Context
SLS2 (Swiss Light Source) storage ring injection
    Event sequence observability issue
    Solution – custom asynchronous logging system
SwissFEL timing external network load
    Network overload issue
    Solution – EPICS CA gateway

## Slide 3: Context
Timing and Events systems at Paul Scherrer Institute, Switzerland
Hardware
PSI timing systems are based on Micro-Research Finland (MRF) HW:
  SwissFEL: VME-300 series
  SLS: New in-house board based on cPCI-Serial. EVM Firmware ported by Jukka Pietarinen and Till Straumann

## Slide 4: Context
Software
The main timing application is fully based on EPICS. It takes care of generating and configuring each event sequence executed by the HW, synchronised to the machine repetition rate.
Therefore, the EPICS-based application is critical.

## Slide 5: SLS2 Storage Ring injection
paul.scherrer.institut

## Slide 6: SLS2 Storage Ring injection
In the synchrotron’s storage ring, electrons circulate in fixed slots (called RF buckets).
Over time, some slots become empty and must be refilled. This is detected by the filling pattern feedback system, which determines where injection is needed.
The timing master is responsible for refilling the correct RF bucket by precisely timing the injection chain (Linac, Booster Ring, Storage Ring).
To do so, it sends the identifiers of the slots to be refilled to the EVR downstream via the data buffer.
Storage Ring
Electron bunch train

## Slide 7: SLS2 Storage Ring injection
Filling Pattern Feedback system
Timing Master
External Synchronisation
AC
RF reference
PSI GPAC3 board: simple communication over optical fiber
Timing stream:
Events
Next RF bucket index via data buffer
EPICS based timing master application
Control sequence loop communicates with Filling Pattern feedback.
Set local timing to next RF bucket.
Send the next RF bucket via data buffer.
Emit the EVR synchronisation event, telling all EVR to set their timing to the next RF bucket

## Slide 8: SLS2 Storage Ring injection
Issue
The timing master is critical: wrong bucket injection directly impacts machine operation. Debugging is critical, especially for filling pattern feedback mode.
Standard logging (errlogPrintf) introduces latency and non-deterministic behavior.
Need non-intrusive, local observability without disturbing the real-time process, in order to verify that the correct RF bucket is applied.
Must integrate with EPICS to provide an expert diagnostic tool usable during operation.

## Slide 9: SLS2 Storage Ring injection
Solution – custom asynchronous logging system
For the development of filling pattern feedback, an EPICS asynchronous logging system was designed:
Message creation called from aSub record: evtSeqLogPrintMsg().
Allocate a slot from a fixed-size message pool, drop if empty (non-blocking, locked by mutex).
Message added to FIFO queue, signal EPICS event to notify consumer thread.
Asynchronous low-priority consumer thread: wait on event, dequeue messages one by one.
EPICS waveform record update: messages are copied to the record via BPTR field.
Message is recycled.

## Slide 10: SLS2 Storage Ring injection
# SR Injection log waveform
record(waveform, "$(P)SR-Inj-Debug-I") {
field(DTYP, "EVT SEQ LOG")
}
record(aSub, "$(P)FP-Local-Update_") {
field(SNAM, "fp_local_update") # in src/fp_local.c
[…]
}
In src/fp_local.c
if(sts_debug) evtSeqLogPrintMsg(“…%d”,var);
Template
Source

## Slide 11: SwissFEL timing external network load
Context
SwissFEL timing master generates the timing event sequence at a repetition rate of 100 Hz.
It is based on IOxOS IFC1210 (VME).
Originally, it was protected from high network load using a Soft IOC, acting as a gateway.

## Slide 12: SwissFEL timing external network load
Issue – Disproportionate impact
Over the years, the soft IOC was bypassed, and clients started using directly the local master PVs.
The timing master became overloaded and often missed FEL pulses (more than 500 CA clients, and up to 9000 connections).
This triggered an RF interlock, and caused an RF phase loss, interrupting the machine for 30 minutes.
This is a known risk as the timing master is a single point of failure. However, the problem escalated significantly and cannot be justified to operations.

## Slide 13: SwissFEL timing external network load
Solution - EPICS CA gateway
Traditional CA gateway deployment, with IOC in another subnet is not convenient: We cannot justify creating a subnet for a single IOC.
From the original documentation, we noticed that the gateway can be used to isolate an IOC.
It is not necessary to use it to access PVs across subnets.
This is the basic application of this EPICS extension, which is sometimes forgotten.
The timing master can then be hidden by changing its default port.

## Slide 14: SwissFEL timing external network load
Machine network
Timing master
IOC
Non-default port: 5092
EPICS ca-gateway
Soft IOC
Default port: 5064
Clients
CA (port 5064)
CA (port 5092)
epicsEnvSet SYS "SIN-TIMAST"
### Hide IOC behind gateway
# Change IOC default server and beacon ports
epicsEnvSet("EPICS_CAS_SERVER_PORT","5992")
epicsEnvSet("EPICS_CAS_BEACON_PORT","5993")
# Setting CA port is not mandatory, but is done for consistency, and to
# prevent accidental exposure on default port (5064)
epicsEnvSet("EPICS_CA_SERVER_PORT","5992")
epicsEnvSet("EPICS_CA_BEACON_PORT","5993")

## Slide 15: SwissFEL timing external network load

## Slide 16: SwissFEL timing external network load

## Slide 17
Thank you for your attention.
Any questions?
If you are interested by the sources of the asynchronous logging system, or want to discuss timing systems or other topics: romain.vallotton@psi.ch