## Slide 1: StreamDevice Introduction
Dirk Zimoch :: Paul Scherrer Institut
EPICS Collaboration Meeting April 2026

## Slide 2: What is StreamDevice?
One generic EPICS driver for many different devices

## Slide 3: How can a Device Driver be Generic?
Separate similarities from differences
What do many devices have in common?
Command strings
Human readable Text
Fixed size (binary) “telegrams”
Limited set of buses
Serial (RS232, RS485, USB)
GPIB
Ethernet (TCP, UDP)
What is different between those devices?
Command sets
Command words
Terminators
Value encoding
Formatting
Position in the command
Configuration
Programming

## Slide 4: StreamDevice Architecture
StreamDevice
waveform
...
serial
TCP
GPIB
asynDriver
…
stringout
bo
ai
%f
%b
%{…}
%<…>
%/…/
Modular design allows to plug in new functionality
This is already done
This is already done
Record database (templates)
Protocol file
Startup script
This is what you need to do

## Slide 5: StreamDevice and asynDriver
Does StreamDevice replace asynDriver?
  No. In fact it uses asynDriver to talk to the hardware.
  To be exact: It uses the asynOctet interface.
But doesn’t asynDriver already come with device support?
  Yes, but for string-based devices only stringin, stringout and char waveform.
https://github.com/epics-modules/asyn
StreamDevice does the string formatting and parsing and asynDriver does the hardware access.
https://github.com/paulscherrerinstitute/StreamDevice
Example:
ao VAL=3.1415
StreamDevice
3.1415 (double)
"SET %.2f\r\n"
"SET 3.14\r\n" (string)
asynDriver
RS232

## Slide 6: Example: Read a Device in 3 Easy Steps
Read Kelvin temperature #1 from a LakeShore 218 via RS232
  Command: "KRDG? 1" CR LF
  Reply: "+273.15" CR LF
Configure serial port in startup script
      drvAsynSerialPortConfigure LakeShore1 /dev/ttyS0
      asynSetOption LakeShore1 0, baud 9600
      asynSetOption LakeShore1 0, …
Write a protocol file, e.g. file LS218.prot
      Terminator = CR LF; temp_K_1 { out "KRDG? 1"; in "%f"; }
Write a record connecting to protocol file, protocol, and port
      record (ai, "$(DEVICE):TEMP1") {
      field (DTYP, "stream") field (INP, "@LS218.prot temp_K_1 LakeShore1") field (EGU, "K")
      field (PREC, "2") }

## Slide 7: Protocol Files
Have one file for each device type
  Best name it after device type
Set some global configuration of communication properties
Write one protocol for each function/command of device
Use out and in commands send and receive strings
Format/parse values with format converters like %f.
  Format converters work on implicit variables, typically VAL or RVAL fields.
  You can redirect to other fields or even other records
See: https://paulscherrerinstitute.github.io/StreamDevice/protocol.html
#LakeShore 218
Terminator = CR LF; ReplyTimeout = 1000; #ms ReadTimeout = 100; #ms
reset { out "*RST"; #no reply wait 2000; }
# read in Kelvin temp_K_1 { out "KRDG? 1"; in "%f"; }
# read in Celsius temp_C_1 { out "CRDG? 1"; in "%f"; }
Configuration variables
Protocol needs unique name within file
Comment: # until end of line
write constant string
read and parse reply string
if used by an ai record %f sets .VAL

## Slide 8: Strings in StreamDevice
Strings can be single or double quoted.
  "That's a string"
  'This one too'
Strings can be written in chunks, with or without comma
  "This is", ' one' " big" ' string'
Non-printable characters can be written in many ways: hex, oct, or dec number, escape sequence, symbolic name
  0x0a 012 10 "\x0a" "\012" "\10" "\n" LF NL
  0x00 0 "\x00" "\0" NUL
Alternatives can be freely mixed
  0x1b "00", 'PR3' CR
See: https://paulscherrerinstitute.github.io/StreamDevice/protocol.html#str
This is the way to break long strings into multiple lines.
For a list of symbolic names and escape sequences see the documentation.
Only difference: no need to escape the other quote type

## Slide 9: Formats as Known From printf/scanf
Standard formats
  %f, %e, %E, %g, %G, %d, %i, %x, %o, %s, %c, %[…]
  standard flags %0 -+# to modify format and %* to skip input
  new flags %? for optional input and %= for input comparison
  but no type modifiers like %hi or %lf
Additional formats and features
  %b (bit strings like "10010001")
  %r (raw machine format numbers)
  %{…|…|…} (enumerations)
  %<…> (checksums)
  %/…/ (regular expressions)
Variable is implicit, usually VAL or RVAL field
  Depends on converter type and record type
  Can be redirected like %(EGU)s or %(record)f
See: https://paulscherrerinstitute.github.io/StreamDevice/formats.html
These are just some examples.
More formats can be added.
"redirection" is explained later

## Slide 10: Protocol Parameters
Passing parameters from record to protocol can save typing.
Example: LakeShore218 has 8 temperatures
Terminator = CR LF; temp_K_1 {out "KRDG? 1"; in "%f";} temp_K_2 {out "KRDG? 2"; in "%f";} temp_K_3 {out "KRDG? 3"; in "%f";} temp_K_4 {out "KRDG? 4"; in "%f";} temp_K_5 {out "KRDG? 5"; in "%f";} temp_K_6 {out "KRDG? 6"; in "%f";} temp_K_7 {out "KRDG? 7"; in "%f";} temp_K_8 {out "KRDG? 8"; in "%f";}
Terminator = CR LF; temp_K {out "KRDG? \$1"; in "%f";}
record(ai,"$(DEVICE):TEMP2") {
field(DTYP,"stream") field(INP,"@LS218.prot temp_K(2) $(PORT)") field(EGU,"K") field(PREC,"2") }
Use parameter instead: "\$1" is 1st parameter
Pass value for 1st parameter
Up to 9 parameters possible.
record(ai,"$(DEVICE):TEMP2") {
field(DTYP,"stream") field(INP,"@LS218.prot temp_K_2 $(PORT)") field(EGU,"K") field(PREC,"2") }

## Slide 11: Redirections
Normally format converters choose field automatically
  VAL or RVAL, depending on format data type
  Scaling (ASLO, AOFF) and smoothing (SMOO) are supported
But sometimes other fields or even other records are needed
  e.g. when one message contains more than one value.
Examples:
  Write value and units: out "%f %(EGU)s";
  Read status and value: in "%(otherrecord)d,%f";
Other records must be on the same IOC.
Use parameters to avoid full record names in protocols.
  Like "%(\$1)d" or "%(\$1:STATUS)d"
If no field is given .VAL is assumed
pass full record name as parameter
pass only part of record name as parameter

## Slide 12: Redirection Example
Example: "position?" request gives reply with 6 coordinates. "position( 1.2 , 2.1234, 23.12 ,-2.312 ,-12.33 ,24.4321)"
pos { out "position?"; in "position(%f\_," "%(\$1:POS-Y)f\_," "%(\$1:POS-Z)f\_," "%(\$1:POS-RX)f\_," "%(\$1:POS-RY)f\_," "%(\$1:POS-RZ)f\_)";}
record (ai,"$(DEV):POS-X") {
field (DTYP,"stream") field (INP, "@$(PROT) pos($(DEV)) $(PORT)") field (EGU, "mm") field (PREC,"2") field (SCAN,"5 second")
field (FLNK,"…")
}
record (ai,$(DEV):POS-Y) {
field (EGU, "mm")
field (PREC,"2")
}
…
record (ai,$(DEV):POS-RZ) {
field (EGU, "deg")
field (PREC,"3")
}
When FLNK is processed, the other records have already got their values.
These records have SCAN="Passive" and DTYP="Soft Channel"
When redirecting to .RVAL use
DTYP="Raw Soft Channel"
Redirecting to other records uses dbPutField() and thus process the target if the field (here .VAL) is PP
Spaces around numbers:
%f accepts leading whitespace. Any amount of trailing whitespace is consumed by \_.

## Slide 13: Complex Protocol: Pfeiffer MaxiGauge
Send device address (on RS485) ESC (=0x1b) "aa"
  aa is address 00, 01, …
Send pressure read command: "PRn" CR
  n is sensor number 1 … 6
Each command is acknowledged with ACK (=0x06) CR LF
After acknowledge request value with ENQ (=0x05)
Receive status and pressure: "0,1.234E-5" CR LF
InTerminator = CR LF; # no OutTerminator because of ENQ pressure { out ESC "0\$1" "PR\$2" CR; in ACK; out ENQ; in "%(\$3:STATUS)d,%f"; }
sensor
record (ai,"$(D):PRESSURE") {
field (DTYP,"stream") field (INP, "@Maxi.prot pressure($(A),$(S),$(D)) $(B)") }
record (mbbi,"$(D):STATUS") { field (ZRST,"OK") field (ONST,"Unterrange") field (TWST,"Overrange")
… }
pass address, sensor and device name as 3 parameters
address
redirect status to other record

## Slide 14: Enum Format: %{…|…|…}
Translates integers to enumerated strings and back
Example1: Device can be switched with "STOP" and "GO".
Example2: Device may run forward or backward with different speeds (e.g. 1 or 5 mm/s) and reports this as "<<", "<", "=", ">", or ">>".
See: https://paulscherrerinstitute.github.io/StreamDevice/formats.html#enum
switch { out "%{STOP|GO}"; }
speed { out "DIR?"; in "DIR=%#{<<=-5|<=-1|\=|>>=5|>=1}" }
record (bo,"$(DEV):SWITCH") {
field (DTYP,"stream") field (OUT, "@XXX.proto switch $(PORT)") field (ZNAM,"off") field (ONAM,"on") }
record (longin,"$(DEV):SPEED") {
field (DTYP,"stream")
field (INP, "@XXX.proto speed $(PORT)") field (EGU, "mm/s")
}
0 = "STOP" 1 = "GO"
%#{ allows assignments: "<<" = -5 "<" = -1 "=" = 0 ">" = 1 ">>" = 5
Escape any literal | or } or = or \ in enum strings as \| or \} or \= or \\
>> before > to avoid wrong match
Input not matching any string raises INVALID/CALC alarm

## Slide 15: Binary Protocols (aka “Telegrams”)
Example: Send/receive 5 bytes telegrams:
  Address, command, 2 bytes value (little endian), xor-checksum
  Confirmation is the same with bit 8 set in command byte
Use %r to send integers in “raw” machine code format
set_value { MaxInput=5; out $1 0x04 "%#.2r%<xor>"; in $1 0x84 "%=#.2r%<xor>"; }
get_value { MaxInput=5; out $1 0x44 0x00 0x00 "%<xor>"; in $1 0xc4 "%2r%<xor>"; }
pass address as parameter 1 (no \ outside quotes)
%= checks reply value
Add checksum
Test checksum
local configurations per protocol (overwrite globals)
details on %r see next slide
Protocol does not use Terminators but has fixed size messages and checksums.

## Slide 16: Raw values: %r and %R
Output format: %<flag><width>.<precision>r
  flag #: little endian (default is big endian)
  width: number of bytes printed (sign extended, default 1)
  precision: number of bytes taken from variable (default 1)
Example: value = 0xdeadbeef
  out "%2r"; 0xff 0xef 1 byte sign extended to 2
  out "%.2r"; 0xbe 0xef 2 bytes
  out "%#.4r"; 0xef 0xbe 0xad 0xde 4 bytes little endian
  out "%#4.2r"; 0xef 0xbe 0xff 0xff 2 bytes sign extended to 4
Input format: %<flag><width>r
  width: number of bytes to read
  flag #: little endian
  flag 0: zero extend to long (default is sign extend)
%4R is float and %8R is double
See: https://paulscherrerinstitute.github.io/StreamDevice/formats.html#raw
Pitfall !
sorry for the mess out "%.2r" versus in "%2r"

## Slide 17: Checksums: %<…>
Many types of checksums supported
  sum, xor, crc (8,16,32 bit), adler32, …
Output: checksum is appended to output
Input: checksum is compared with input
Range selection: %<start>.<end><checksum>
  start: number of bytes to skip from beginning of string (default 0)
  end: number of bytes to skip just before %<...> (default 0)
Example: out "Example string%3.2<xor>";
Flag %0<…> switches to hex digits instead of raw bytes
Flag %#<…> switches to little endian for multi-byte checksums
See: https://paulscherrerinstitute.github.io/StreamDevice/formats.html#chksum

## Slide 18: Regular expressions: %/…/
Regular expressions allow very powerful string parsing
  either to read the string itself
  or to find data that comes after some string
Example: Read title of a web-page. drvAsynIPPortConfigure "web","epics.web.psi.ch:80”
See: https://paulscherrerinstitute.github.io/StreamDevice/formats.html#regex
OutTerminator = LF; ExtraInput = ignore;
title { out "GET http://\$1"; in "%.1/(?im)<title>(.*?)<\/title>/"; disconnect; }
record (stringin, "$(DEV):TITLE") {
field (DTYP,"stream")
field (INP, "@web.prot title(epics.web.psi.ch) web")
}
.1: get 1st sub expression, here: (.*?)
escape the /
web server disconnects after sending a page and so do we
%/…/ ignores all input before the match if the expression does not start with ^
don't complain that we don't parse the whole page
(?im): case insensitive multi-line match.
These are Perl compatible regular expressions (PCRE) which are more powerful than Posix or GNU regex.

## Slide 19: Regular expression substitutions: %#/…/…/
Regular expression substitutions let you re-write input or output strings
  Use before other formats in input or after normal formats in output, e.g.: in "%#/(<?=[+-]) +(?=[0-9])//%f" first removes all spaces between signs and numbers, then parses as float.
More Examples:
%#/_/ / replaces all underscores with spaces
%#/:// removes all : characters. (0b:19:35:31:34 becomes 0b19353134)
%#/..\B/&:/ inserts : after every second character which is not at the end of a word. (0b19353134 becomes 0b:19:35:31:34)
%#/\\/\// replaces all \ with / (\dir\file becomes /dir/file)
%#+-10.2/ab/X/ replaces the string ab with X maximal 2 times in the last 10 characters. (abcabcabcabc becomes abcXcXcabc)
%#/([^+-])*([+-])/\2\1/ moves a postfix sign to the front. (1.23- becomes -1.23)ß
%#-2/.*/\U0/ converts the previous 2 characters to upper case.
See: https://paulscherrerinstitute.github.io/StreamDevice/formats.html#regsub

## Slide 20: Asynchronous input: I/O Intr
Some devices send unsolicited data
Example: Temperature sensor sends periodically: "+27.3 C" CR LF
Asynchronous records have SCAN "I/O Intr"
Asynchronous protocols typically have only an in command.
Any input from that device is checked.
  Including input going to other protocols
  Record is processed whenever matching input is found.
  Non-matching input is silently ignored (no error).
Terminator = CR LF;
temperature { in "%f C"; }
record (ai,"$(DEVICE):TEMP") {
field (DTYP,"stream") field (INP, "@$(PROT) temperature $(PORT)") field (EGU, "C") field (PREC,"1")
field (SCAN,"I/O Intr") }

## Slide 21: I/O Intr vs. Redirection
Example: Read input line with two values x and y every second
x { out "xy?"; in "%f %*f"; }
y { in "%*f %f"; }
record (ai,"$(D):x") {
field (SCAN,"1 second") field (DTYP,"stream") field (INP, "@XY.prot x $(PORT)") }
record (ai,"$(D):y") {
field (SCAN, "I/O Intr") field (DTYP, "stream")
field (INP, "@XY.prot y $(PORT)")
}
Ignore second value
Ignore first value
Be careful:
Any input with two numbers matches.
x { out "xy?"; in "%f %(\$1:y)f"; }
record (ai,"$(D):x") {
field (SCAN,"1 second") field (DTYP,"stream") field (INP, "@XY.prot x($(D)) $(PORT)") }
record (ai,"$(D):y") {
field (SCAN, "Passive") field (DTYP, "Soft Channel")
}
y is processed when x writes value to it
redirect second value
Redirection is more selective.
Only input from x goes to y.
y is processed when anyone receives input that matches

## Slide 22: Error Handling
All errors set SEVR to INVALID
  STAT depends on error type
    Reply timeout: device does not reply (TIMEOUT)
    Read timeout: device stops sending unexpectedly (READ)
    Write timeout: writing is not possible (WRITE)
    Lock timeout: port is in use by other records (TIMEOUT)
    Mismatch: input does not match format string (CALC)
Errors abort the protocol
  but may trigger exception handlers
Errors are not propagated along redirections 
  Redirects before mismatch are processed normally
  Redirects after mismatch are not processed at all
  Only active record gets error status
Mismatch in "I/O Intr" records is silently ignored

## Slide 23: Exception Handlers
Jump to different protocol if something goes wrong
  @mismatch, @replyTimeout, @readTimeout, @writeTimeout
Example: Device replies with value or error message
readValue { out "value?"; in "%f"; @mismatch { in "%(\$1:ErrorString)39c"; } }
if input does not match "%f" jump to @mismatch
reparse input and redirect
record (ai,"$(DEVICE):Value") {
field (DTYP,"stream") field (INP, "@$(PROT) readValue($(DEVICE)) $(PORT)") }
record (stringin,"$(DEVICE):ErrorString") { }
Exception handlers can be defined before or inside normal protocol.
If input does not match and the @mismatch handler starts with in, then the same input is parsed a second time.

## Slide 24: Record Initialization
Output records can be initialized from hardware
  Initialization is formally handled as an exception: @init
getVolt { out "VOLT?"; in "VOLT %f"; }
setVolt { out "VOLT %.2f"; @init {getVolt;} }
getFreq { out "FREQ?"; in "FREQ %f MHZ"; }
setFreq { out "FREQ %.6f MHZ"; @init {getFreq;} }
@init is executed in iocInit before scans are started and at re-connects.
record (ai,"$(D):ReadVoltage") {
field (DTYP,"stream") field (INP, "@X.prot getVolt $(PORT)") }
record (ao,$(D):SetVoltage") { field (DTYP,"stream") field (OUT, "@X.prot setVolt $(PORT)") }
record (ai,"$(D):ReadFrequency") {
field (DTYP,"stream") field (INP, "@X.prot getFreq $(PORT)") }
record (ao,$(D):SetFrequency") { field (DTYP,"stream") field (OUT, "@X.prot setFreq $(PORT)") }
reference other protocol to insert all its commands

## Slide 25: Arrays
For arrays the format is repeated for each element with optional separator string in between.
Example: "{10.2,345.3,23.3,10.0}"
Input
  reads max NELM elements
  at least one element must be found
  sets NORD to number of elements found
Output
  writes NORD elements
readArray { Separator = ","; in "{%f}"; }
record (aai,"$(DEVICE):Array") {
field (FTVL,"FLOAT")
field (NELM,"100") field (DTYP,"stream")
field (INP, "@$(PROT) readArray $(PORT)") }

## Slide 26: Recommended Reading
StreamDevice documentation
    https://paulscherrerinstitute.github.io/StreamDevice
AsynDriver documentation:
    https://epics-modules.github.io/master/asyn
EPICS Documentation
    https://docs.epics-controls.org/projects/base/en/latest/index.html
    Record Reference
      https://docs.epics-controls.org/projects/base/en/latest/ ComponentReference.html#record-type-definitions
Getting started with EPICS
  https://docs.epics-controls.org/en/latest/getting-started/EPICS_Intro.html