## Slide 1: Acoustic Newtonian noise modelling in the caverns of ET
L.Maurin, F.Gautier, S.Terrien, M.Barsuglia
Journées ET France, 01/04/2026
f5=4.8Hz

## Slide 2
Acoustic in Gravitational Wave detectors
Radiation pressure fluctuation
Suspension Thermal noise
Seismic noise
Newtonian noise
Residual gas
Diffuse light
Quantum noise
Substract brownian noise
Coating thermo-optic noise
Vibrations or vibroacoustic coupling path
- Vibrations of technical origin contribute to Seismic noise
- Treated by superattenuator (or active control)
One possible cause of Newtonian Noise
- The pressure field variations generates change of mass density => Acoustic has a gravity counterpart
- Impossible to shield
Scattered or diffused light can couple with vibroacoustic
- Vibrations of optical benches, vibrations of viewport induced by structure borne sources
Cause of beam jitter at Injection

## Slide 3
HVAC system
heating ventilation and air conditioning
airborne source
  responsible for acoustic noise
structure borne source
  responsible for ground/walls vibrations
Air flow
Local turbulence
Generation of acoustic
disturbances (pressure pulsations)
Acoustic radiation by inlets/outlets
Equivalent monopolar source
Horn geometry
HEPA filter
Simulation of acoustic field
Clear modal behavior below 30Hz
Positions of inlets/outlets are key factors
Sound generation in the experimental halls
Acoustic + Mechanical vibrations

## Slide 4
Step 1 : Acoustic pressure inside a cavity
Step 2 : induced Gravity potential
Step 3 : induced Gravity field
Density
Gravity field
Virgo - NEB
ET- end cavern
Potential
Estimation of the NN of Acoustic origin – methodology and results
Pressure
Point sources
Acoustic modes of the rigid cavity

## Slide 5
Full model
Model considers the ducts coupled with the room
and are model as harmonic acoustic pistons

## Slide 6
Simplified model
Inlets and Outlets are replaced by monopoles
Amplitude and phase are estimated from full model

## Slide 7
Acoustic field
Potential of gravity field
Function
Function
Modal basis
Functional basis
Modal and functional basis using the simplified model

## Slide 8
Acoustic field
Gravity field
Modal basis
Gradient of Psi
Function
Function
Modal and functional basis using the simplified model

## Slide 9
What is the impact of the Newtonian noise on the suspended test mass?
Streamlines for the gravity field in the room in the 2D
cross-section at one meter from the ground.
NN estimate
Strain =
Estimating the newtonian noise from the simplified model
y
z
x

## Slide 10
Acoustic absorption of walls
Rotation speed of Hvac
Absorption is described as a modal damping factor
Acoustic pressure level generated by rotating fan follows a power law (n = 3)
How to limit the newtonian noise

## Slide 11
The dominant acoustic source is the HVAC
The HVAC is described by a set of equivalent monopoles where the closest to the fan are the most contributing to acoustic noise
A modal model describes properly the measured acoustic pressure field
A computation scheme is developed to estimate the newtonian noise from acoustic origin
Estimated NN is found to be lower than the current Virgo sensitivity
What do we learn from Virgo ?

## Slide 12
Einstein Telescope (ET) - layout and sensitivity
Artist view of ET – Triangle configuration
Credits : M. Kraan
Geometry of an end cavern
ET design sensitivity
Order of magnitude: 10-24@10Hz
ETLF and ET HF baseline sensitivity

## Slide 13
Acoustic modal basis of an end cavern
f1=0Hz
f2=1.2Hz
f3=2.2Hz
f4=4.3Hz
f5=4.8Hz
f6=6.3Hz
f7=6.9Hz
f8=7.1Hz
High acoustic modal density due to the large size of the room
Remarks
  The cave is supposed airtight and disconnected from the tunnel
  The sound inside tunnel is ignored, but the acoustic modal density inside is enormous

## Slide 14
Functional basis for the gravity field
f1=0Hz
f2=1.2Hz
f3=2.2Hz
f4=4.3Hz
f5=4.8Hz
f6=6.3Hz
f7=6.9Hz
f8=7.1Hz
Numerous longitudinal modes => orientation of the NN gravity field is mostly in the laser beam direction

## Slide 15
Angular filtering of the gravity functions
Azimut Angle
Elevation Angle
y
z
x

## Slide 16
Angular filtering of the gravity functions
4,88
6,38
6,99
7,18
9,26

## Slide 17
Simulated NN of acoustic origin – effect of the inlets/outlets positions
Configuration 1
Integration of the Virgo sources inside the ET cavern
Test of 2 configurations for the inlets/outlets
Configuration 2
6 inlets
2 outlets
NN level reach the design sensitivity curve

## Slide 18
Simulated NN of acoustic origin – effect of acoustic absorption
Adding acoustic absorption helps to limit NN
In practice, acoustic absorption at low frequency is very difficult to achieve
Melamine foam
Wiremesh

## Slide 19
Simulated NN of acoustic origin – effect of the fan rotation speed
Air flow variation
The fan rotation speed is the most influent parameter on the noise level (power law)
Simulations for
  Virgo’s source amplitude
  2 x Virgo
  0.5 x Virgo
=> The methodology can be used to estimate the maximum acoustic threshold

## Slide 20
4,88
6,38
6,99
7,18
8,02
8,65
8,88
9,26
9,74
10,68
11,29
11,81
Identification of problematic acoustic modes

## Slide 21
4,88
6,38
6,99
7,18
8,02
8,65
8,88
9,26
9,74
10,68
11,29
11,81
Identification of problematic acoustic modes
Modes with azimut angle <10°

## Slide 22
How to kill NN before the construction ?
Even modes
(symmetric)
Odd modes
(antisymmetric)
Mirror
Mass distribution is equal on each side of mirror, NN cancels out
Mass difference between each side is maximum, high NN coupling
Plane of symmetry
To kill NN :
Even modes : Place sensitive equipment on antinode
Odd modes : Place Acoustic sources on node

## Slide 23
Impact of tower diameter on NN
Reduction of NN coupling is expected with increase in tower diameter
=> Negligible impact below 20 Hz

## Slide 24
Extension to mechanical vibration

## Slide 25
ET’s preliminary design
Acoustic is currently not a design criterion

## Slide 26
Concluding remarks
HVAC is necessary for the thermal stability, air cleanliness and also for the health of operators
Acoustic noise due to HVAC induces Newtonian Noise, visible by ET
Acoustic Newtonian noise must be considered as an issue in the design of Einstein Telescope’s cavern
The developped approach can give insight
  on the geometry of caverns, tuning of the length for minimizing the gravity perturbation at mirror’s location
  on the positions of the inlets/outlets, tuning to minimize the acoustic excitation
  on the positions of the towers
  on the specifications of the HVAC

## Slide 28
Classification of acoustic modes for ET
8,65
8,88
9,26
9,74
11,29
11,81
Transverse
Others
4,88
6,38
6,99
7,18
8,02
10,68
Longitudinal

## Slide 29
Classification of acoustic modes
Even modes
(symmetric)
Odd modes
(antisymmetric)
Mirror
Plane of symmetry

## Slide 30
Classification of acoustic modes for ET
4,88
6,38
6,99
7,18
8,02
10,68
Symmetrical
Asymmetrical
Longitudinal
Symmetry Plane

## Slide 31
How to reduce NN coupling
3 strategies to counter acoustic Newtonian Noise :
Positioning of sources and sensitivite equipment
Geometric optimisation of the room
Geometric optimisation of vacuum tower shape
S
T
4,88

## Slide 32
Positioning of sources and sensitive equipment
4,88
S
T
S
T
S
T
Study of 3 configurations :
Initial configuration
Source on acoustic node
Tower on acoustic antinode

## Slide 33
Positioning of sources and sensitive equipment
S
T
S
T
S
T

## Slide 34
Geometry of the room
S
T
T
S
T
Increase in length of the cavern

## Slide 35
Geometry of the room
S
T
T
S
T
Increase in length of the cavern
Length increase

## Slide 36
Geometry of the room
S
T
T
S
T
Increase in length of the cavern
Length increase

## Slide 37
Geometry of the room
S
T
T
S
T
Increase in length of the cavern

## Slide 38
Geometry of the tower
S
T

## Slide 40
Room acoustic characteristics (TR60, fs, α)
North End Building
AHU room
SAS
Experimental area
Simplified geometry of the experimental area
Concrete
Concrete + resin
Steel/wool/Steel sandwich
Reverberation time
TR60 = 4.7 s
Schroeder frequency
Fs = 50 Hz
Modal acoustics if f < 50Hz
Average absorption coefficient
𝝰 = 0.097
M. Falxa et al, 2018* => acoustic characterization
*VIR-0673A-18
Frequency (Hz)
TR60 (s)

## Slide 41
Goal: Modeling Newtonian noise due to building acoustics
WEB map
Red and blue dot indicate microphones
Context of the study
Main acoustic source is an HVAC (heating ventilation and air conditioning) centrifugal fan

## Slide 42
Gravity field:
Potential:
Density fluctuation:
Modal basis expansion of the gravity field
Acoustic field
Potential of gravity field
Modal basis
Functional basis

## Slide 43
Simulated NN of acoustic origin – effect of acoustic absorption
Adding acoustic absorption helps to limit NN
In practice, acoustic absorption at low frequency is very difficult to achieve
Melamine foam
Wiremesh