## Slide 1
ALICE-ITS3
Etude thermique carte électronique

## Slide 2
Objectifs présentation
Modélisations d’un système thermofluidique
Comparaison entre les modèles et des résultats expérimentaux

## Slide 3
Problématique
Des composants des cartes dissipent de la puissance thermique : P1 à P11 (total 4.4 W )
Un Flux d’air passe sur les cartes vers le détecteur
La température des chips ne doit pas dépasser 60°C
La puissance thermique transmise par les cartes à l’air circulant vers le détecteur ne doit pas dépasser 10% de la puissance générée par les cartes
Détecteur
°C
qair=1 l. mn-1
Puissance théorique VS réelle ?

## Slide 4
Vias cuivre ep 0.018mm
Choix techniques
Refroidissement par circulation d’eau
Plaque cuivre
Pad thermique ou colle entre les vias et la plaque cuivre
Vias
°C
Plaques cuivre ep 0.035mm

## Slide 5
Choix techniques
Composants refroidis par eau
Composants refroidis par air

## Slide 6
Alalyse préliminaire
Températures des chips
Puissance thermique transmise à l’air environnant
Objectifs de l’étude
Conduction dans les solides avec résistances thermiques d’interfaces
Convection forcée air autour de la carte
Convection eau par circulation dans les tubes
Type d’étude

## Slide 7
Alalyse préliminaire
Type de modélisation ?
Paramètres les plus influents ?
Orientations de l’étude
Modèle 1 D
Modèle 3D EF thermique
Modèle 3D thermofluidique

## Slide 8
Modèle 1 D
Modèle 1 D

## Slide 9
Modèle 1 D
Ordres de grandeur
Elévation de température eau : DT) → DT

## Slide 10
Modèle 1 D Puissance Th air
Ordres de grandeur
Puissances thermiques échangées avec l’air environnant :
6 Chips :
Autres composants P= 0.745 W
Plaque Cuivre
Tubes eau
PCB
P = 0.150 W
P= 0.120W
P= -0.120W
P= 0.240W
4
1
2
2
3
5
Bilan : 1.135 W (26%)

## Slide 11
°C |  | 0.03 | 0.03 | 6 | 4.8 | 23.8
 |  | 0.03 | 0.03 | 6 | 4.8 | 23.8
Modèle 1 D Temp chips
Ordres de grandeur (Chip 6)
Gradients de température
Eau
Tube
Brasure
Plaque cuivre
TIM
Via
P
Chip
°C | .15 | 16.67 | 16.70 | 16.73 | 22.73 | 27.53 | 51.33
 |  | 16.67 | 16.70 | 16.73 | 22.73 | 27.53 | 51.33
Valeurs de puissances corrigées en fonction des mesures

## Slide 12
Modèle 1 D
Outil LTspice
Dédié aux calculs électroniques
Adaptable à la thermique
Permet le recalcul après changement des paramètres

## Slide 13
Modèle 1 D
Modèle 3 D
Thermique

## Slide 14
General simulation parameters
Geometry : Here is the electronic card to study. It has been simplified in order to keep only significant components. Caps over the 6 chips are not represented. The calculation geometry is composed of : Vias, Cu cooling plate, cooling pipe.
Item | Real conditions | Thermal study
Thermal loads | Thermal power on the 11 chips | Thermal power on the 6 upper faces of the vias of the main 6 chips
Cooling source | Water circulation/ T=[16.0]°C at inlet, q=0.2 l. mn-1 | Convection / water on pipe inner surfaces T=[16.0]°C constant h=2000W.m-2.K-1
Ambient air exchange |  | 
Cu plate | Air flow/T=17.0°C at inlet, q=1 l. mn-1 | Convection /air on upper Cu plate, T=17.0°C, h=30W.m-2.K-1
Pipes | Air flow/T=17.0°C at inlet, q=1 l. mn-1 | Convection /air on pipe outer surfaces , T=17.0°C, h=30W. m-2.K-1
Chips | Air flow/T=17.0°C at inlet, q=1 l. mn-1 | Convection /air on vias upper surfaces, T=17.0°C, h=30W. m-2.K-1
No PCB

## Slide 15
Thermal model geometry and mesh
Geometry - mesh
Stainless steel pipe 3.0 x 2.5 mm
Copper plate 0.2mm thick
Copper plates 0.035mm thick
Copper vias 0.018mm thick
Pipe + Cu plate : solid elements (ref Ansys=279)
Vias (plates and cylinders) : shell elements (ref Ansys=131)

## Slide 16
loads
Thermal loads applied on thermal model

## Slide 17
Thermal connections
Thermal pad (Gap Pad® 5000S35 ) Cu cooling Plate / Cu via plates : l=5W. m-1.K-1 , so, h=10000 W.m-2.K-1
Internal connections
Stainless steel pipe brased on Cu Plate : l=70W.m-1.K-1 , so h=70000 W.m-2.K-1

## Slide 18
Thermal boundary conditions for thermal model
Convection / air on pipe outer surfaces and Cu plate upper surface ( T=17°C, h=30 W.m-2.K-1 )
Boundary conditions
Convection / water on pipe inner surfaces T=16,0°C, h=2000 W.m-2.K-1

## Slide 19
Temperature field
Results

## Slide 20
Temperature gradient / thermal pad
Results
The average temperature gradient along the pad thickness is ~7.15°C
Via side
CU plate side

## Slide 21
Temperature vias
Results
Température max vias 65°C

## Slide 22
Thermal balance
Results
Item | Power source / power exchanged | P spec (W) | P FEA result (W) | % total power | Flow
1 | P Vias | 3.73 |  | 100 | → system
2 | P convection / vias air |  | -0.012 |  | system →
3 | P convection pipe inner face water |  | -3.700 |  | system →
4 | P convection pipes outer face air |  | 0.061 |  | → system
5 | P convection Cu cooling plate air |  | -0.078 |  | system →
8 | P balance |  | -3.73 | -100 | 

## Slide 23
Modèle 3 D
Thermofluidique

## Slide 24
Mesures

## Slide 25
Mesures
Banc 1 seule carte
Banc 2 cartes

## Slide 26
Mesures vs Simulations
°C |  | 48.9 | 44.9 | 46.7 | 45.3 | 57.4
 |  | 48.9 | 44.9 | 46.7 | 45.3 | 57.4
°C | 27.6 | 25.5 | 24.7 | 25.0 | 26.7 | 24.6
% | 35% | 48% | 45% | 46% | 41% | 57%
 | 27.6 | 25.5 | 24.7 | 25.0 | 26.7 | 24.6
% | 35% | 48% | 45% | 46% | 41% | 57%
Simulation 3D
Mesures
 | 0.457 | 0.573 | 0.510 | 0.539 | 0.514 | 1.136
 | 0.457 | 0.573 | 0.510 | 0.539 | 0.514 | 1.136
°C | 23.5 | 23.5 | 22.8 | 23.4 | 23.6 | 24.9
 | 23.5 | 23.5 | 22.8 | 23.4 | 23.6 | 24.9
°C | 27.4 | 26.2 | 24.9 | 25.2 | 25.2 | 26.9
 | 27.4 | 26.2 | 24.9 | 25.2 | 25.2 | 26.9
1 carte
2 cartes
Carte 1
Carte 2
°C |  |  |  |  |  | 51.3
 |  |  |  |  |  | 51.3
Simulation 1D

## Slide 27
Merci de votre attention

## Slide 28
Annexe

## Slide 29
Specifications – loads –
Thermal loads – details